ENGINEERING SPECIFICATION

SYMCOM MODEL LSRX-C

AC Current Sensor

- GENERAL

  - REFERENCES

    - UL 508 Industrial Control Equipment – Underwriters Laboratories

    - IEC 60947 Low Voltage Switchgear and Controlgear – International Electrotechnical Commission

    - CSA C22.2 No. 14 Industrial Control Equipment – Canadian Standards Association

    - ANSI/IEEE C62.41 – American National Standards Institute/Institute of Electrical & Electronics Engineers

  - WARRANTY

    - Manufacturer Warranty:  The manufacturer shall guarantee the equipment to be free from material and workmanship defects for a period of five years from the date of manufacture when installed and operated according to the manufacturer’s requirements.

- PRODUCTS

  - MANUFACTURERS

The equipment specified shall be the Model LSRX-C, manufactured by SymCom, Inc.

  - DESCRIPTION

    - Regulatory Requirements:

1.   The equipment shall be UL certified:

        - The equipment shall be UL Listed as type NKCR—Industrial Control   Equipment-Motor Controllers-Auxiliary Devices.

  - Performance/Design Criteria:  AC CURRENT SENSOR

    - Capabilities and Features:

      - Inputs

        - The equipment shall accept single-phase operating current rated 5-200 amps.

      - Outputs

        - The equipment shall include one Form A (SPST) output relay. Contacts pilot duty rated 480VA@240VAC.  Contacts general purpose rated 5A@240VAC.

      - Functional Specifications

        - The equipment shall energize the output contacts when greater than 4.5 amps are present.

        - The equipment shall include an electrical life of 1x105 operations at rated load.

        - The equipment shall include a mechanical life of 1x107 operations.

        - The equipment shall include one depluggable terminal block.

        - The equipment shall include one LED indicator light.  The light will illuminate when the relay contacts are energized.

    - Electromagnetic Compatibility:

      - The equipment shall be immune to electrostatic discharge per IEC 61000-4-2, Level 2, 4kV contact discharge and 4kV air discharge.

      - The equipment shall be immune to electrical fast transient bursts per IEC 61000-4-4, Level 3.  Specified limits shall be 2kV power supply port, 1kV input/output ports.

      - The equipment’s power supply port shall be immune to electrical surges per IEC 61000-4-5, Level 3.  Specified limits shall be 2kV line-to-line and line-to-ground.

      - The equipment shall be immune to radiated radio frequency emissions.  Specified limits shall be 10V/m at 150 MHz.

    - Dielectric Isolation:  Equipment withstands an alternating current potential of 1000V plus twice the rated voltage of the equipment for 1 minute without breakdown between uninsulated live parts and the enclosure with the contacts open and closed; between terminals of opposite polarity with the contacts closed; and between uninsulated live parts of different circuits.

    - Environmental Requirements:

      - The equipment shall operate continuously without derating in ambient temperatures of -20° to 70°C (-4° to 158°F).

      - The equipment shall operate continuously without derating in relative humidity of up to 95% non-condensing per IEC 68-2-3.

      - The equipment shall operate properly after storage in ambient temperatures of -40° to 80°C (-40° to 176°F).

    - Dimensions:  The equipment dimensions shall not exceed 2.70” H x 1.13” W x 2.50” D.

    - Enclosure class of protection:  The equipment shall provide IP20 (finger safe) protection.

    - Mounting:

      - The equipment shall be surface mountable.

End of Section